## Sheet1
Planned Preventive Maintenance schedule
Activity & Location | Frequency | [52 empty] | LEGEND | time axis 2014-04-01 to 2015-03-24
In House | Week | [52 empty] | D | Daily | time axis 2014-04-01 to 2015-03-24
Inspect perimeter gates & fencing | W | [52 empty] | W | Weekly
Inspect internal fire doors & final exits doors | W | [52 empty] | M | Monthly
Inspect Playground | W | [52 empty] | 3M | 3 Monthly
Check fire alarms call points | W | [52 empty] | T | Termly
Check H & C water services | W | [52 empty] | 6M | 6 Monthly
Log/Record all Utility Meter Readings | M | [52 empty] | 6M | 6 Monthly | bar: 2014-04-22; 2014-05-20; 2014-06-24; 2014-07-22; 2014-08-26; 2014-09-23; 2014-10-21; 2014-11-25; 2014-12-23; 2015-01-20; 2015-02-17; 2015-03-24
Legionella Monitoring Tasks to be Recorded | [53 empty] | Y | Yearly
Little used outlets flush through and purge | W | [52 empty] | 5Y | 5 Years
Sentinel Taps H/W should be at least 50°C | M | bar: 2014-04-01; 2014-04-29; 2014-05-27; 2014-06-24; 2014-07-22; 2014-08-19; 2014-09-16; 2014-10-14; 2014-11-11; 2014-12-09; 2015-01-06; 2015-02-03; 2015-03-03
Sentinel Taps C/W should be below 20°C | M | bar: 2014-04-01; 2014-04-29; 2014-05-27; 2014-06-24; 2014-07-22; 2014-08-19; 2014-09-16; 2014-10-14; 2014-11-11; 2014-12-09; 2015-01-06; 2015-02-03; 2015-03-03
TMV's where fitted H/W should be 50°C on entry | M | bar: 2014-04-01; 2014-04-29; 2014-05-27; 2014-06-24; 2014-07-22; 2014-08-19; 2014-09-16; 2014-10-14; 2014-11-11; 2014-12-09; 2015-01-06; 2015-02-03; 2015-03-03
Water leaving Calorifer should be at least 60°C | M | bar: 2014-04-01; 2014-04-29; 2014-05-27; 2014-06-24; 2014-07-22; 2014-08-19; 2014-09-16; 2014-10-14; 2014-11-11; 2014-12-09; 2015-01-06; 2015-02-03; 2015-03-03
Water returning Calorifer should be at least 50°C | M | bar: 2014-04-01; 2014-04-29; 2014-05-27; 2014-06-24; 2014-07-22; 2014-08-19; 2014-09-16; 2014-10-14; 2014-11-11; 2014-12-09; 2015-01-06; 2015-02-03; 2015-03-03
Shower heads/hoses dismantle & clean/descale | M | bar: 2014-04-01; 2014-04-29; 2014-05-27; 2014-06-24; 2014-07-22; 2014-08-19; 2014-09-16; 2014-10-14; 2014-11-11; 2014-12-09; 2015-01-06; 2015-02-03; 2015-03-03
Incoming cold water inlets should be below 20°C | 6M | bar: 2014-07-08; 2014-10-28
Service & Re-commission Thermostatic Mixing Valves | Y | bar: 2014-08-19
Fire Safety Monitoring
Check indicator/alarm panel showing normal | D
Check all exits can be opened | D
Check all Fire door for damage & obstruction | D
Check push bars & pads work correctly | W
Check routes are safe | W
Check electronic release mechanisms | M | bar: 2014-04-15; 2014-05-13; 2014-06-10; 2014-07-08; 2014-08-05; 2014-09-02; 2014-09-30; 2014-10-28; 2014-11-25; 2014-12-23; 2015-01-20; 2015-02-17; 2015-03-17
Check fire door seals | M | bar: 2014-04-15; 2014-05-13; 2014-06-10; 2014-07-08; 2014-08-05; 2014-09-02; 2014-09-30; 2014-10-28; 2014-11-25; 2014-12-23; 2015-01-20; 2015-02-17; 2015-03-17
Check all escape route clear of obstruction | M | bar: 2014-04-15; 2014-05-13; 2014-06-10; 2014-07-08; 2014-08-05; 2014-09-02; 2014-09-30; 2014-10-28; 2014-11-25; 2014-12-23; 2015-01-20; 2015-02-17; 2015-03-17
Fire safety meetings with Head and other staff | T | bar: 2014-04-08; 2014-07-08; 2014-10-14; 2015-01-13
Fire Safety Tasks to be Recorded
Test fire alarm system when occupied at least 30 sec | W
All call points to be tested every 13 weeks | W
Fire / Evacuation Drill carried out and recorded | T | bar: 2014-04-29; 2014-07-29; 2014-10-28; 2015-01-27
Fire Risk Assessment or Review | Y | bar: 2014-09-09
Fire Fighting Equipment
Fire fighting equipment check present & correctly placed | D
Fire extinguisher check for damage & securely fixed | W
Emergency Lighting to be Recorded
Check charging indicators are visible | W
Test system | M | bar: 2014-04-01; 2014-04-29; 2014-05-27; 2014-06-24; 2014-07-22; 2014-08-19; 2014-09-16; 2014-10-14; 2014-11-11; 2014-12-09; 2015-01-06; 2015-02-03; 2015-03-03
Asbestos
Walk areas and visually inspect | 3M | bar: 2014-04-08; 2014-07-08; 2014-10-07; 2015-01-06
Asbestos Audits "4Thought" review & update | Y | bar: 2014-07-22
Electrical
Portable Appliance Testing PAT | Y | bar: 2014-05-27
Inspection of Lightning Protection System | Y | bar: 2014-09-16
NICEIC Fixing Wiring Inspection & Testing (Satisfactory) | 5Y
Other
Inspect Car Parks | M | bar: 2014-04-01; 2014-04-29; 2014-05-27; 2014-06-24; 2014-07-22; 2014-08-19; 2014-09-16; 2014-10-14; 2014-11-11; 2014-12-09; 2015-01-06; 2015-02-03; 2015-03-03
Inspect gates | M | bar: 2014-04-08; 2014-05-06; 2014-06-03; 2014-07-01; 2014-07-29; 2014-08-26; 2014-09-23; 2014-10-21; 2014-11-18; 2014-12-16; 2015-01-13; 2015-02-10; 2015-03-10
clean food bins | T | bar: 2014-06-10; 2014-09-09; 2014-12-09; 2015-03-10
clean leaves from gutters | T | bar: 2014-05-20; 2014-08-19; 2014-11-18; 2015-02-17
Clean Gulley & drains | T | bar: 2014-05-20; 2014-08-19; 2014-11-18; 2015-02-17
Inspect roofs (Visual) | T | bar: 2014-05-20; 2014-08-19; 2014-11-18; 2015-02-17
Run H & C taps for 1 Minute | T | bar: 2014-04-01; 2014-07-01; 2014-09-30; 2014-12-30
Walk/ test protected alarm areas | T | bar: 2014-04-01; 2014-07-01; 2014-09-30; 2014-12-30
Check locks, catches & bolts | T | bar: 2014-05-13; 2014-08-12; 2014-11-11; 2015-02-10
Test panic buttons | T | bar: 2014-05-13; 2014-08-12; 2014-11-11; 2015-02-10
Inspect roof storage tanks | T | bar: 2014-05-13; 2014-08-12; 2014-11-11; 2015-02-10
Ladder Checks | 6M | bar: 2014-04-29; 2014-10-28
Review Energy Conservation Practices | 6M | bar: 2014-04-29; 2014-10-28
Other Contracts
Lift Inspections & Services | M | bar: 2014-04-15; 2014-05-13; 2014-06-10; 2014-07-08; 2014-08-05; 2014-09-02; 2014-09-30; 2014-10-28; 2014-11-25; 2014-12-23; 2015-01-20; 2015-02-17; 2015-03-17
Fire alarm service | 3M | bar: 2014-04-01; 2014-07-01; 2014-09-30; 2014-12-30
Air conditioning | 3M | bar: 2014-04-01; 2014-07-01; 2014-09-30; 2014-12-30
Boiler service | 6M | bar: 2014-04-29; 2014-10-28
Water system check | Y | bar: 2014-05-13
Inspect fire fighting equipment | Y | bar: 2014-09-09
Intruder alarm check | Y | bar: 2014-10-28