## Sheet1
Planned Preventive Maintenance schedule
Activity & Location | Frequency | 2014-04-01 | 2014-04-08 | 2014-04-15 | 2014-04-22 | 2014-04-29 | 2014-05-06 | 2014-05-13 | 2014-05-20 | 2014-05-27 | 2014-06-03 | 2014-06-10 | 2014-06-17 | 2014-06-24 | 2014-07-01 | 2014-07-08 | 2014-07-15 | 2014-07-22 | 2014-07-29 | 2014-08-05 | 2014-08-12 | 2014-08-19 | 2014-08-26 | 2014-09-02 | 2014-09-09 | 2014-09-16 | 2014-09-23 | 2014-09-30 | 2014-10-07 | 2014-10-14 | 2014-10-21 | 2014-10-28 | 2014-11-04 | 2014-11-11 | 2014-11-18 | 2014-11-25 | 2014-12-02 | 2014-12-09 | 2014-12-16 | 2014-12-23 | 2014-12-30 | 2015-01-06 | 2015-01-13 | 2015-01-20 | 2015-01-27 | 2015-02-03 | 2015-02-10 | 2015-02-17 | 2015-02-24 | 2015-03-03 | 2015-03-10 | 2015-03-17 | 2015-03-24 | LEGEND
In House | Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | D | Daily
Inspect perimeter gates & fencing | W | [52 empty] | W | Weekly
Inspect internal fire doors & final exits doors | W | [52 empty] | M | Monthly
Inspect Playground | W | [52 empty] | 3M | 3 Monthly
Check fire alarms call points | W | [52 empty] | T | Termly
Check H & C water services | W | [52 empty] | 6M | 6 Monthly
Log/Record all Utility Meter Readings | M | [52 empty] | 6M | 6 Monthly
Legionella Monitoring Tasks to be Recorded | [53 empty] | Y | Yearly
Little used outlets flush through and purge | W | [52 empty] | 5Y | 5 Years
Sentinel Taps H/W should be at least 50°C | M
Sentinel Taps C/W should be below 20°C | M
TMV's where fitted H/W should be 50°C on entry | M
Water leaving Calorifer should be at least 60°C | M
Water returning Calorifer should be at least 50°C | M
Shower heads/hoses dismantle & clean/descale | M
Incoming cold water inlets should be below 20°C | 6M
Service & Re-commission Thermostatic Mixing Valves | Y
Fire Safety Monitoring
Check indicator/alarm panel showing normal | D
Check all exits can be opened | D
Check all Fire door for damage & obstruction | D
Check push bars & pads work correctly | W
Check routes are safe | W
Check electronic release mechanisms | M
Check fire door seals | M
Check all escape route clear of obstruction | M
Fire safety meetings with Head and other staff | T
Fire Safety Tasks to be Recorded
Test fire alarm system when occupied at least 30 sec | W
All call points to be tested every 13 weeks | W
Fire / Evacuation Drill carried out and recorded | T
Fire Risk Assessment or Review | Y
Fire Fighting Equipment
Fire fighting equipment check present & correctly placed | D
Fire extinguisher check for damage & securely fixed | W
Emergency Lighting to be Recorded
Check charging indicators are visible | W
Test system | M
Asbestos
Walk areas and visually inspect | 3M
Asbestos Audits "4Thought" review & update | Y
Electrical
Portable Appliance Testing PAT | Y
Inspection of Lightning Protection System | Y
NICEIC Fixing Wiring Inspection & Testing (Satisfactory) | 5Y
Other
Inspect Car Parks | M
Inspect gates | M
clean food bins | T
clean leaves from gutters | T
Clean Gulley & drains | T
Inspect roofs (Visual) | T
Run H & C taps for 1 Minute | T
Walk/ test protected alarm areas | T
Check locks, catches & bolts | T
Test panic buttons | T
Inspect roof storage tanks | T
Ladder Checks | 6M
Review Energy Conservation Practices | 6M
Other Contracts
Lift Inspections & Services | M
Fire alarm service | 3M
Air conditioning | 3M
Boiler service | 6M
Water system check | Y
Inspect fire fighting equipment | Y
Intruder alarm check | Y